8.i

1)))))1

beamlines

Fyzikální ústav AV ČR, v. v. I., Na Slovance 2, 182 21 Praha 8

1nfo@elibeams eu  I www.eli beams.eu

Confidentiality

BL  - Restricted for

| Level | interna/ use |  |  |
| --- | --- | --- | --- |
| Branch | M - Management | Document Status | Document Released |
| Level | Process ( M,Q,S) | Valid from (date) | 01.06.2020 |
| Document Type | Directive |  |  |
| PBS Code | NOT RELEVANT |  |  |

TC ID  /  TC Revision	00272188  / A

WBS /OBS Code	97  Technology Infrastructure and Services

D1R20

ELI na,ne convention and addressing for electrical co111ponents

Keywords

Conductor,  cabinet, UID

Position	Name	Signature	Date

Prepared by  Electrical Engineer	Vojtěch Gaman

Quality Engineer	Jan Černý	2 1. 5 . 20 20

o

Head of Electrical Engineering Luboš Nims	 		/tf,j\

Agreed by

Assurance

Team Leader  - Laser

beamlines control system

group	Alexander Jack Nylon

Quality	Quality Manager	Viktor Fedosov

v

Approved	Project Manager	Roman Hvězda

by

t.S- 5"'_ w-i.,O

### eii

##### 1)))))1

beamlines

Fyzikální ústav AV ČR. v. v. i., Na Slovance 2, 182 21 Praha 8

1n fo@elibeams.eu I www e i beams.eu

| Revision History I Change Log |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Change No. | Made by | Date | - - Change description, Pages, Chapters |  | TC rev. | Ver. |
|  |  |  | - |  |  |  |

| Reviewed By |  |  |  |
| --- | --- | --- | --- |
| Name (Reviewer) | Position | Date | Signature |
| Roman Kuřátko | Facility Manager | J1...S. | ,.1.-r _ |
| Birgit Plotzeneder | Control System Team Leader | .;i .i\· c.;. 2o ;ltJ | Í7iL |
| Pavel Bakule | Head of department 97 | z,..r, J. Z.o Le | /J J ---'2_ |
| Veronika Olšov cová | Safety Team Manager | u.r:uw | /l |
| Ivo Konderla | Quality Engineer - | 11.r. 1-t>'t.o | I |
| Matyáš Žalud | Electrical Designer | 21. . lotO | Jíf\J)) |
| Martin Nešpor | Control System Technician | t, 1 . f' . la 2e | .A- |
| Lukáš Mindl | Designer - Electrical | lz.s,Zozo |  |
| Michal Suchý | Electrician | )) , f.JOíL | t„0· |
| Karel Zíka | Technology Installation Engineer | 2 2 . r-..2..oz..o | /q |

... ""'li•• • ,•	..     \       ,_..."  • .,. r-,.    "	'•	'	.',   1'

I           -               •            •    -

<lt_-

6)

| FZU | lnstltuteofPhysrcs |  |
| --- | --- | --- |
|  | Academy of Scr | ences |

\	I A	·	-  ·.

T-C 002721 88

Pag    : 2 /    12 , .  . -	.

oftheCzcch   .

.

;,"'\

•.

Versron 01

The Czech Academ

of Sc1·ences

Valici from:  01.06.2020	.

# Eii

#### 1)))))1

beamlines

Fyzikální ústav AV ČR, v. v. i., Na Slovance 2, 182 21 Praha 8

1n fo@eli beams.eu I www eli beams.eu

Tahle of Content

- Purpose	4

- Scope	4

- Glossary of Abbreviations and Terms	4

- Related documents	4

- Naming convention	4

  - Components abbreviations	4

  - UIDs marking	5

5.3.   Numbering   systems   for   components  ..........................................................  S

5.3.1.          PLCs.................................................................................................       S

    - Connection terminals	7

    - Filters, Power supplies, Circuit breakers and Surge protectors connected to mains (230V/400V)	7

    - DIN rails	8

    - Relays, SPDs, Contactors and Fuses	9

  - Addressing	9

    - Printed labels	9

- Conductors requirements	11

  - Signal conductors (providing just information in 24V logic) + analogue conductors	11

  - Power conductors permanently energized with low voltage (up   to SOV)	12

  - Power conductors  -  mains (230/400V)	12

- Database	12

- Attachments	12

r.,_,	•       '-   '

0

ge·

.   .

- .	·

I

.-•     -   "-	r	-	-->,.  •   •	•	-	_,-      • -	•

FZU

..

TC 0 2_72188   A	.

h

Institute of Physlcs

oftheCzech

T  e Czech Academy

O	CleOCeS

fs  .

·	Pa     3  /   12	"

\

Vers1on 01

Valid  from:  01.06.2020	._,	.

Acaderny of Sciences

Eii beamlines

Fyzikální ústav AV ČR, v. v. i., Na Slovance 2, 182 21 Praha 8

, nfo@eli beams eu I www eli beams.eu

1.Purpose

This directive sets standards for name convention, addressing and type of electrical components, cabinets, IT racks, conductors and similar devices used in EU   Beamlines.

###### 2.Scope

This document is valid for all EU Beamlines employees for installations in laser and experimental  halls.

This document does not directly deal with mains installation (230/400V) as this is described by general electrical standards [1,   2].

This directive is not valid for cabinets installed prior to release of this directive and for these in scope of facility that follow general electrical standards  [1,    2].

###### Glossary of Abbreviations and Terms

| Abbr. | Term | Explanation |
| --- | --- | --- |
| - | EU Beamlines employees | Employees of Fyzikální ústav AV ČR, v.v.i., organizationally assigned to section 9 - EU Beamlines |
| UID | Unique identification number | A unique identification code for all electrical devices in laser and experimental halls. |

- Related documents

[1].	ČSN 332130:2014, ed.3 Low-voltage electrical installations -  Interna! electric distribution lines

[2].	ČSN 332000:2009, ed. 2 Low-voltage electrical installations

[3]. ČSN EN 60445:2017, ed. 5 Basic  and  safety  principles  for  man-machine  interface, marking and identification - Identification of  equipment  terminals, conductor  terminations  and conductors

###### Naming convention

  - Components abbreviations

Ali components in cabinets have unique abbreviations and follow the convention   below:

  - A=  PLCs

  - D  = DIN  rails

  - F = Fuses

  - FA =  Circuit breakers for  mains (230/400V)

  - FLT =  Filters for mains (230/400V)

  - FV  =  Surge protectors  for mains (230/400V)

  - G  = Power supplies

  - KA = Relays

  - KM  = Contactors

  - R = Cabinets

  - SPD  = Signal surge protectors  for  low voltage (up  to  SOV)

"              -·•	,	;,

...._,,,.f'i.

h       ,,._      I	•	-;	•1.:Jt• 1,.-,:'     ;    41   •       -	-     •	-	•          CCf             ..	--    -               •           -	..,	.._'      -      .\I  •    •      "': , 1  . U.•  •	..	111       •	•         ,.               i,.,,	,   •	,

'.  .,	.  .

| FZU |  |
| --- | --- |
|  | ! ! ! e sc,ences _ ,.... |

.	TC 00272188/  , A ·  _ _.....	.	.	··.	.,+· .	·  ·.:.	:.

.	Page:  4  /  1. 2 ,  -,  -:

0

V	·	01

o  ···,:	, .

lnstltuteofPhyslcs

The Czech Academy

V

erls,.dofn	.  01  06 2020	·

of Sciences

a I   rom.	.	.	.

..-.:

eli

1)))))1

beamlines

Fyzikální ústav AV ČR. v. v. i., Na Slovance 2, 182 21 Praha 8

1n fo@eli beams eu I www eli beams.eu

- UPS  = Uninterruptible  power supplies

- X  = Connection terminals

  - UIDs marking

The UID marking is preferably used for cabinets, PLCs and UPSs. The UID is generated according to the key ABnn where A stands for abbreviation (Chapter 5.1) /function of  the device (Chapter 5.3.1 for PLCs), B stands for the system prefix defined in table (Tahle 1) and nn is a serial number in the system  -    examples:

- R801 -  cabinet number 01 in experimental  hall E3

- I0H501 -  IOH is a function  of PLC, 5 means that it  is related to BT and 01 that  it is the first PLC in the  system

- RI0403 -  RIO is a function of PLC, 4 means that it is related to L4 and 03 that     it is the third PLC in  the system

Tahle 1: System prefixes for  generating  UID

| System | Ll | L2 | L3 | L4 | BT | El | E2 | E3 | E4 | ES | Plant rooms |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| System prefixes | 1 | 2 | 3 | 4 | s | 6 | 7 | 8 | 9 | 10 | 11 |

Other components inside cabinets that have some parameters have also a unique UID created using the same convention. Examples of such components: SDS and  NSW.

  - Numbering systems for components

    - PLCs

PLC itself is marked by its label (UID) that typically starts with its function IOH, RIO, CRIO, PLC, etc. This label is directly attached to the device and it not used during addressing.

PLCs cards are marked nAm, where n is a serial number of PLC in  a cabinet and m is  a serial number of a card. The exception is the first power supply card that is an integral part of PLC.

For B&R components, this first power supply card is marked by nA.PS. The m = 1, 2, etc. is used for  rest of the cards including further power supply    cards.

Additionally, when PLC contains network module next to the cards, this network module is marked nA.BC or .HB. If there is more such modules then a serial number is added from left to right (example for first PLC in the cabinet - 1A.BC1, 1A.BC2, etc.). The network inputs of such modules if they do not have original marking are marked IFl, IF2, etc. (used only during addressing, not marked on the device itself). Example of such PLC, type from company B&R - Figure 1.

FZU

Institute of Physlcs oftheCzech Academy of Sciences

6)

| 2721 |  |  |
| --- | --- | --- |
|  | 5/ | 1 |
| on 01 |  |  |

•	.:	•	...	,5"         ... ,..,	'

0

ge:

.

TC 0

ers

Pa

88 / A	.

he

Q

|  | Czech Academy |
| --- | --- |
| T |  |
|  | CleOCeS |

2

f

.

V  . ,	O S

Valtd from: 01.06.2020	#    ..  -

Si

1)))))1

beamlines

Fyzikální ústav AV ČR, v. v. i., Na Slovance 2, 182 21 Praha 8

1nfo@eli beams.eu  I www eli beams.eu

Figure 1: PLC IOH501 type B&R with 1 network module and 3 power supply    cards

Other examples of PLCs, type from company PILZ -  Figure 2 and type from company  NI  -  Figure 3. (lA.*,  * depends on exact marking on the  device, e.g.   1A.X1).

Figure 2: PLC801 type PILZ

::·} f t 002·i2iaa / Á

..

J

FZU

lnstl tute of Phys lc Acaderny of sc1ences

The Czech Academy

of Sc1·ences

Q

-. ,:.	g :6 I  12	6)

oftheCzech   .

·  ,

.	Vers,on 01

; •   t  t Valid  from: 01.06.2020

# Eii

##### 1)))))1

beamlines

Fyzikální ústav AV ČR, v. v. I., Na Slovance 2, 182 21 Praha 8

1n fo@eli beams eu I www e i beams.eu

CRI0503

Figure 3: PLC CRI0503 type  NI

    - Connection terminals

The function name of the connection  terminal is preferable  added after  the marking   X

- examples:  XSACB,  XDPWR.G52_24V, XDPWR.G52_COM,  XTEMP,  XTMPS, XSCON,

etc. When it is not required to add the specific function name these connection  terminals are marked Xl,  X2 ... Xn (n  is a serial number in the   cabinet).

When more of the same connection terminals are in the cabinet, then a serial number   is added after the  marking.

Inside a cabinet, it is possible to  mark connection terminals by labels with or without  DIN rail number, which they are mounted  on -  Figure 4.  Both variants are    allowed.

oz

,-i

(/)

u

X

o

,-i

Figure 4: 3 connection terminals XSCON on DIN rail Dl and two possible ways of marking  -  A) marking  with DIN rail nr. B) marking  without  DIN rail  nr.

    - Filters,	Power	supplies,	Circuit	breakers	and	Surge protectors  connected  to  mains (230V/400V)

Components - circuit breakers (FA), power supplies (G), filters (FLT) and surge protectors (FV) connected to mains (230/400V) are numbered by the convention below to indicate which branches are powered based    on various laser states (scenarios)

  - Numbering G/FA/FLT/FV101-199 for no emission laser state   (scenario)

nario)

d

Numbering G/FA/FLT/FV201-299 for low power laser state   (sce

A,!f'7.' )

•t:

•       .:.p..

·r-:,,.1

•

7

.  o

e ers

1

1

A

1· -··

;

I

-·.

,

. :

| TC | 00 |  | 2721 |  |  | 8, 8 |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | / |  |  |
| V | ,o |  | n |  |  |  |

-  · ...·.Pa.g , :	,2	.

"Th

· .·

o

s

czechAca emy

T'         ...:',	-	,;_...._-;:;.   •   -	-;.       ",.	•    •         ._	•	•  •       .;   _,.-    -...,;   -"• -

---.:  ·. · •.

e

lnstituteofPhyslcs ofthe Czech AcademyofSc1ence

.·... ..·	.

FZ.U·

.

Valtd from. 01.06.2020

f S   .

O	ClenCeS

.

1)))))1

beamlines

Fyzikální ústav AV ČR. v. v. i., Na Slovance 2, 182 21 Praha 8

1n fo@eli beams eu I www e1i beams.eu

- Numbering G/FA/FLT/FV301-399 for high power laser state   (scenario)

- Numbering G/FA/FLT/FVSOl-599 for powered by UPS laser state  (scenario)

Designer can choose additional system (e.g. 401-499) for  components  operated  in other laser states (scenarios) if he considers it as useful  or better arranged. In  that  case, he must create a note describing his system on the electrical    drawing.

Other components that refer to neither above-mentioned options have a serial number set by a designer; see the example of cabinet with UPS - Figure   5.

| FAS - FVS ,- FASl | - UPS501 1- FASll - FLTSll | - G511 |
| --- | --- | --- |
| 1 | 1- FA512 • FLT512 | - GS12 |
|  | I- FA513 • FLT513 | - G513 |
|  | I- FA514 • FLT514 | - G514 |
|  | L FA515 • FLT515 | - GS15 |
| L FA52 | - KMl 1 - FAS21 - FLT521 I- FA522 - FLT522 | - G521 |
|  | 1- FA523 - FLT523 |  |
|  | I- FA524 - FLT524 |  |
|  | 1- FA525 - FLT525 |  |
|  | 1- FAS26 - FLT526 |  |
|  | L FA527 - FLT527 |  |

Figure 5: Part of circuit with UPS

    - DIN rails

DIN rails are marked Dl,  D2 ... Dn (n  is a serial number in a cabinet) in direction from  up to down and subsequently  from the left to right -  Figure    6.

Figure 6: Example of cabinet with DIN   rails

# Eii

#### 1)))))1

beamlines

Fyzikální ústav AV ČR. v. v. i., Na Slovance 2, 182 21 Praha 8

nfo@eli beams eu I www e i beams.eu

    - Relays,  SPDs, Contactors  and Fuses

These components are marked according  to the  convention  that all components  have a serial  number starting from  1:

- Relays are numbered KA1, KA2 ... KAn (n is a serial number in a  cabinet).

- Contactors are numbered KM1, KM2 ... KMn (n is a serial number in a  cabinet).

- SPDs are numbered  SPD1, SPD2 ... SPDn  (n  is  a serial number in a   cabinet).

- Fuses are numbered Fl,  F2 ... Fn (n is a serial number in a  cabinet).

  - Addressing

Conductors between components in cabinets are marked according the convention defined in Tahle  2.

Tahle  2: Addressing convention

| Conductor start |  |  | Conductor end |  |  |
| --- | --- | --- | --- | --- | --- |
| Start Address | separator | End Address | End Address | separator | Start Address |
| Dn.Qn.x |  | Dm.Qm.y | Dm.Qm.y |  | Dn.Qn.x |

Dn.Qn.x : Dm.Qm.y

- Dn -  DIN rail with serial number  n at conductor   start

- Dm  -  DIN rail with serial number m at conductor   end

- Qn -      component Q with serial number n and pin x at conductor start

- Qm -      component Q with serial number m and pin y at conductor end

- The marking is mirrored on each  end

- If the conductor comes from different cabinet, the cabinets UIDs are added before both numbers RO.Dn.Qn.x : RP.Dm.Qm.y (RO is the UID of the first cabinet and RP is the UID of the second  cabinet).

- Examples:

o	D1.1A1.11: D1.2A3.1

o	D1.XTEMP1.8:D2.KA1.1

o	R510.D1.1A1.5:R513.D7.KA127.A1

o	D10.XSACB13.20:D3.XDPWR.G51_24V

o	D6.KA57.A1:D1.2A.X2.3

    - Printed labels

ge:

h

fs

.

Vers1on 01

·,-c 00272188 /

Pa   . 9/  12

oftheCmh

Acaderny of Sc1en

ces

.

FZU Institute of Physlcs

o

Conductors are preferably marked by printed plastic labels from the printing machine Weidmuller Printjet ADVANCED. The manual for this device is attached, see [AP02]. Experiment  Control  Systems dpt. is responsible  for  production  of these  printed labels

A

.	.  .

..

.

T e Czech Academy

:.,"

\

Valid from: 01.06.2020	._,

.	O	ClenCeS

€li

1)))))1

beamlines

Fyzikální ústav AV ČR, v. v. i., Na Slovance 2, 182 21 Praha 8

1nfo@el1 beams.eu  I www eli beams.eu

and define the suitable type of labels for components/conductors (examples  of labels  are on Figure  7).

Figure 7: Types of labels for Weidmuller Printjet  ADVANCED

Printed labels are placed as close as possible to conductor terminals (must be still easily readable). The marking is printed on two lines, example on Figure 8 and Figure 9.

KA1

( pin 2)

Labe! on conductor start:

I

/

1A1

(pin 1)

I DI N fil	l-

Dl  I

Labe! on cond uct or end:

Figure 8:  General scheme of printed labels from the printing machine    Weidmuller

Figure 9:  Example of printed labels from the printing  machine   Weidmuller

2

.

?,.

FZU

In case of additional changes/reworks in fieldworks or lack of space for  two  lines, it might be necessary to use shrink/sleeve tubes labels from the mobile printing device Brother that prints complete addressing label on only one line. These labels are placed again  as close  as possible  to  conductor  terminals.  On vertical  components as relays

- I                   •

cr  00 7  218 8 / A

...	.	:	.	' ;. .   "  '\ .	..  '-" .

·

P'age:

o l / 12	·

ofPhy s lcs	6)

The Czech

Academy

10

| Instit | ute |  |
| --- | --- | --- |
| ofthe | C | zech |

. Vers1on	of Sť   nces

- Valid   from:   01.06.2020	,.	:-.	Q	AcademyofSc1ences	,e

## Eli

##### 1)))))1

beamlines

Fyzikální ústav AV ČR. v. v. i., Na Slovance 2, 182 21 Praha 8

1nfo@el1 beams eu  I  w w w.eli beams.eu

and connection terminals the labels are placed  on upper side from right direction  and  on down side from left direction, example on Figure    10.

.R_ea_d fro_m l_eft _side>

<--

Read from right side

Figure 10:  Example of shrink/sleeve tubes labels from the device   Brother

- Conductors  requirements

Conductors  for cabinets and IT  racks are divided into these three main   categories:

  - Signal conductors (providing just information in 24V logic) + analogue conductors

  - Power conductors permanently energized with low voltage (up to   SOV)

  - Power conductor  -  mains (230/400V)

The conductors colours are defined by this directive (mentioned RAL values are only informative). The cross sections are only   recommended.

  - Signal  conductors  (providing	just  information  in	24V logic) + analogue conductors

These conductors have different requirements than power conductors. The conductors have to  be stranded,  with crimped ferrule on both  ends.

  - General digital signals

    - Colour  -  White (e.g.  RAL 9010)

    - Cross section - O. 50 mm2

  - Personnel Safety signals

    - Colour -  Yellow (e.g. RAL 1021)

    - Cross section -  0.50 mm2

The Czech

of Sciences

Academy

o

'-f   _-\  Te   00272188  / .A	,-	.

p a

/

·

·  V g e :	11 01 12

Valici from: 01.06.2020

FZU lnstltuteofPhyslcs	"

ers,on	oftheCzech

Academyofsc,ences

eli

1)))))1

beamlines

Fyzikální ústav AV ČR. v. v. i., Na Slovance 2, 182 21 Praha 8

nfo@eli beams eu I www eli beams eu

  - Machine Safety signals

    - Colour -  Orange (e.g. RAL 2003)

    - Cross section -  0.50 mm2

  - Analogue signals

    - Colour -   Violet (e.g. RAL 4005)

    - Cross section -  0.50 mm2

  - Power	conductors	permanently	energized	with	low voltage (up to SOV)

The cross section of conductors for low voltage (up to SOV) is selected by a designer and the cross section corresponds to relevant current flow. The conductors have to be stranded,  with crimped  ferrule on both ends.

  - Positive Voltage

    - Colour -  Red -  (e.g. RAL 3000)

    - Cross section -  0.50 /  0.75 /  1.50 mm2

  - Negative Voltage

    - Colour -  Dark Blue -  (e.g. RAL  5002)

    - Cross section -  0.50 /  0.75 /  1.50 mm2

  - Power conductors -  mains (230/400V)

The conductors for mains (230/400 V) follow standard [3].

- Database

  - The Database of UID is shared at http://laser-interface.eli-beams.eu/.

- It serves for generating UID.

- The administration of the Database is the responsibility of the Laser dpt.

- The Database manual is attached, see  [APOl].

###### Attachments

[APOl] Laser Interfaces Database Tutorial [AP02] Manual PrintJet ADVANCED

V age:

V a' d  f

erS10n

1 01

I    rom.,

12

01 .06.2020

o

O	ClenCeS

Tfs

e  •zech Academy

P

2/

·

h

C

l

ln s t l   tut e o f Phys l cs

ofthe Czech

AcademyofScience.s

FZU

. .....

6)

TC 00272 88./ A	.	.	-'·'	. y       ••	:'.	•	•	•