| G - Výpočet přitížení |  |  |
| --- | --- | --- |
| Fotovoltaická elektrárna - FVE Místo realizace: Kaplanova 1931/1, 148 00 Praha 11 - Chodov |  |  |
| Investor: Státní fond životního prostředí ČR, Kaplanova 1931/1, 148 00 Praha 11 - Chodov |  |  |
| Stupeň dokumentace: Dokumentace pro výběr zhotovitele (DVZ) |  |  |
| Část: D.1.4 Technika prostředí staveb / D.1.4.1 - Zařízení silnoproudé elektrotechniky |  |  |
| Zhotovitel dokumentace: Rostislav Štark, XXX, www.elros.cz |  | Číslo paré: |
| Zodpovědný projektant: XXX | Datum: 12/2024 |  |
| Vypracoval: XXX | Č. zakázky: 2024-068 |  |

Project report

Projectname	MS-HMR-Kaplanova

### Project Number	Wa_DE_hmRtfwnq

Project Address

1

148 00 Hlavní město Praha

Czech Republic

Creation date:	12/16/2024

Project created by:

Frankensolar Eastern Europe s.r.o. Ke Zdibsku 240

25066 Zdiby

XXX

### Contents

| Planning and liability notice | 3 | - | 3 |
| --- | --- | --- | --- |
| Project Data | 4 | - | 4 |
| Project Location - Google Maps | 5 | - | 5 |
| Building: Building 3D Image - from Screenshot Roof_1 | 6 | - | 6 |
| Roof substructure | 7 | - | 7 |
| PV-Module | 8 | - | 8 |
| Anchor type & model | 9 | - | 9 |
| Racking Parameter | 10 | - | 10 |
| Position | 11 | - | 11 |
| Installation-Plan | 12 | - | 12 |
| Roof coordinates CAD | 13 | - | 13 |
| Roof coordinates | 14 | - | 14 |
| Static CAD | 15 | - | 15 |
| Elevation Parameter Additional Info | 16 | - | 16 |
| Additional Information | 17 | - | 17 |

Climate-friendly TRIC Mounting Systems  LOW CO2

LOW CO2- Climate-friendly Mounting Systems

Sustainable and climate-friendly energy systems are our passion. Now we are taking the next step and continuously reducing our CO2 footprint

We produce our TRIC mounting systems exclusively from certified aluminum products with low CO2 emissions, manufactured in European aluminum plants.

With 4,9 kg of CO2 emissions per kg of (bright) aluminum, the production of our TRIC products generates less than a third of the global average

Regional added value

We also attach great importance to our long-standing partnerships with suppliers from the region. This guarantees not only short transportation routes but also the best product quality

Energy self-sufficient production

TRIC mounting systems are manufactured at our site in Kirchhain in our solar factory, which is 90 percent energy self-sufficient.

Minimal CO2 footprint European aluminum plants Regional added value Short transportation routes Long-term partnerships

Made in Germany

TRIC - LOW CO2

European aluminium plants, regional suppliers and optimization of energy consumption during production - the climate-friendly TRIC assembly systems impress with the lowest CO2 emissions

Less than a third! The low CO2 value is achieved, among other things, through highly efficient electrolysis technology and a high proportion of recycling in aluminum production as well as the consistent use of renewable energy sources.

### Master data

| Project Name | MS-HMR-Kaplanova |
| --- | --- |
| Comment |  |
| Planning Responsible |  |
| Software v.: | 11.0.33.45440 |
| Amount Modules | 88 |
| System Size | 40.48 kWp |
| Orientation [°] | 180 |
| Roofpitch [°] | 2 |
| Allocated Area | 175.33 m² |

Project Address

| Name |  |
| --- | --- |
| Street Address | 1 |
| Postal code | 148 00 |
| City | Hlavní město Praha |
| Phone |  |
| Email |  |
| Notes |  |
| Country | Czech Republic |
| Latitude [°] | 50.03432 |
| Longitude [°] | 14.48788 |
| Altitude [m] | 263 |

Building height h [mm]	16000

Slope of roof [°]	2

Roofing	Membrane roof

Product Type:	TRIC F duo East

System alignment [°]	180

Parapet height [mm]:	100

Parapet width [mm]:	250

### Snow load CSN EN 1991-1-3

Custom(Elev.)

System alignment [°]*

| Snow load [kN/m²]*: | 0.56 |
| --- | --- |
| Slope of roof [°]: | 2 |
| Snow load zone: | I |
| Shape coefficient μi: | 0.8 |

### Wind load CSN EN 1991-1-4 NA:2008

| Wind load [kN/m²]*: | 0.791 |
| --- | --- |
| Terrain Category: | 3 |
| Building height h [mm]: | 16000 |
| Reference Height [mm]: | 16000 |
| Wind zone (see wind zone map): | Area 2 |

PV-Module [Roof_1]

Manufacturer:	Aiko Energy Germany GmbH

Name	AIKO-A460-MAH54Mb

Width [mm]:	1134

Height [mm]:	1757

Thickness [mm]:	30

Framing:	Aluminum

Weight (kg)	21.5

Nominal Power [Watt]:	460

Module Type:	Monocrystalline

Installation:	On Both Sides

Frame color	Black

Temperature coefficient [%/°C]:	-0.26

Efficiency STC:	0.231

Output current MPP - STC [A]:	13.29

Output voltage MPP - STC [V]:	34.62

Short circuit current [A]:	14.25

Open circuit voltage [V]:	41.06

Temperature coefficient Current [%/K]:	0.05

Temperature coefficient Voltage [%/K]:	-0.22

Max. System voltage EU:	1500

Galvanic seperation required:	No

### Clamps [Roof_1]

Mid Clamp:	Modulklemme TRIC clip M27-31 schwarz

End Clamp:	Modulklemme TRIC clip R30 schwarz

Note: Please check to see if the terminal points of the module conforms with the specifications of the manufacturer. If the access points do not match the specifications of the module manufacturer, it is recommended to contact the module manufacturer in conjunction to obtain a release planning. There is no guarantee that the proposed connection is released by the manufacturer.

### Racking Parameter [Roof_1]

Bracket tilt α [°]:	10

Inter-row spacing a [mm]:	205 mm

Friction Constant µ	0.5

The default coefficient of friction used is 0.5 for foil sealing and 0.6 for bitumen sealing membranes and must be verified by the installer or planner. If a lower coefficient of friction is determined on site, this must be applied here for the ballast calculation. The ballast quantity to be applied increases with a lower coefficient of friction. A higher value can be applied up to a maximum of 0.7, provided this has been determined.

Gewicht Ballastierungsstein Schiene	1 kg

Gewicht Ballastierungsstein Ballastbrücke	1 kg

Distance to roof edge [mm]	300

2846

16008

25354

25441

3742

31027

5315

26772

4

5

1

2

3

751

986

1053

13028

16143

1480

13017

2846

16008

25354

25441

3742

31027

5315

26772

751

986

1053

13028

16143

1480

13017

| Coordinate 0 | X: | 0 | Y: | 6621 | Z: | 16000 |
| --- | --- | --- | --- | --- | --- | --- |
| Coordinate 1 | X: | 11220 | Y: | 0 | Z: | 16000 |
| Coordinate 2 | X: | 24357 | Y: | 21685 | Z: | 16000 |
| Coordinate 3 | X: | 25220 | Y: | 21206 | Z: | 16000 |
| Coordinate 4 | X: | 33467 | Y: | 34927 | Z: | 16000 |
| Coordinate 5 | X: | 31070 | Y: | 36462 | Z: | 16000 |
| Coordinate 6 | X: | 43728 | Y: | 58531 | Z: | 16000 |
| Coordinate 7 | X: | 32483 | Y: | 65088 | Z: | 16000 |
| Coordinate 8 | X: | 19922 | Y: | 43736 | Z: | 16000 |
| Coordinate 9 | X: | 18915 | Y: | 42009 | Z: | 16000 |
| Coordinate 10 | X: | 20209 | Y: | 41289 | Z: | 16000 |
| Coordinate 11 | X: | 18292 | Y: | 38075 | Z: | 16000 |
| Coordinate 12 | X: | 17620 | Y: | 38411 | Z: | 16000 |
| Coordinate 13 | X: | 14887 | Y: | 33853 | Z: | 16000 |
| Coordinate 14 | X: | 15798 | Y: | 33325 | Z: | 16000 |

20  17  20 20  2  20 19  4  19 19  3  20 20  2  20 21  20  21

20  17  20 20  2  20 19  4  19 19  3  20 20  2  20 21  20  21

21  20  21 11  20  11 11  20  11 20  1  21 21  4  21

21  20  21 11  20  11 11  20  11 20  1  21 21  4  21

Σ S87.47 kg Σ U150.26 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

4

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S87.47 kg Σ U150.26 kg

Σ S100.22 kg Σ U150.26 kg

Σ S74.13 kg Σ U83.71 kg

20

20

19

19

6

6

21

21

20

20

6

6

5

Σ S74.13 kg Σ U83.71 kg

Σ S74.13 kg Σ U83.71 kg

Σ S100.22 kg Σ U150.26 kg

21

21

21

21

Σ S87.47 kg Σ U150.26 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S87.47 kg Σ U150.26 kg

Σ S100.22 kg Σ U150.26 kg

Σ S74.13 kg Σ U83.71 kg

Σ S74.13 kg Σ U83.71 kg

Σ S74.13 kg Σ U83.71 kg

Σ S100.22 kg Σ U150.26 kg

20  15  20 20  2  20 20  11  11 11  11  20 20  1  21 21  20  21	21  21  21 11  20  11 11  20  11 11  10  21 21  21  21

20  15  20 20  2  20 20  11  11 11  11  20 20  1  21 21  20  21	21  21  21 11  20  11 11  20  11 11  10  21 21  21  21

20  17  20 20  2  20 19  4  19 19  3  20 20  2  20 21  20  21

20  17  20 20  2  20 19  4  19 19  3  20 20  2  20 21  20  21

21  18  21 20  2  20 21  5  21

21  18  21 20  2  20 21  5  21

21  21  21 21  21  21

21  21  21 21  21  21

Σ S87.47 kg Σ U150.26 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

1

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S87.47 kg Σ U150.26 kg

Σ S136.55 kg Σ U150.26 kg

2

Σ S88.92 kg Σ U83.71 kg

Σ S136.55 kg Σ U150.26 kg

Σ S165.39 kg	Σ S165.39 kg

Σ U152.43 kg	Σ U152.43 kg

20

20

19

19

6

6

21

21

14

14

14

14

21

21

21

21

21

21

21 21

21 21

3

21

21

Σ S87.47 kg Σ U150.26 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S87.47 kg Σ U150.26 kg

Σ S136.55 kg Σ U150.26 kg

Σ S88.92 kg Σ U83.71 kg

Σ S136.55 kg Σ U150.26 kg

Σ S165.39 kg Σ U152.43 kg

Σ S165.39 kg Σ U152.43 kg

20  15  20 20  2  20 20  11  11 11  11  20 20  1  21 21  20  21

20  15  20 20  2  20 20  11  11 11  11  20 20  1  21 21  20  21

21  21  21 11  20  11 21  20  21

21  21  21 11  20  11 21  20  21

21  16  21 21  21  21

21  16  21 21  21  21

Total Uplift (U) 5023 kg Total Sliding (S) 4047 kg

Total Amount Stones 5094 (5,094 kg)

Static information: Ballasting [Roof_1]

MS-&shy;HMR-&shy;K... |

12/16/2024

created with

Page 15 / 17

Static V: 11.0.33.45440

### Summary of load parameters [Roof_1]

| Snow load | 0.56 kN/m² |
| --- | --- |
| Wind load | 0.79 kN/m² |
| Friction Constant µ | 0.5 |
| Factor of Safety for Uplift | 1.5 |
| Factor of Safety for Sliding | 1.5 |
| Load factor applied to Dead Load | 0.9 |
| Gewicht Ballastierungsstein Ballastbrücke | 1 kg |
| Anzahl Ballastierungssteine Ballastbrücke | 5094 |
| System surface area | 189.64 m² |
| Roof area | 907.95 m² |
| Total ballast weight | 5,094 kg |
| Weight Module/Rack | 2,423.52 kg |
| Total System weight | 7,517.52 kg |
| Surface load on system area | 0.39 kN/m² |
| Surface load on roof | 0.081 kN/m² |

Planning and liability notice

Please check all inputs and results carefully. It must be ensured that the entries at SUNoptimo match the conditions on site. Since individual peculiarities must be taken into account for each roof, expert clarification must be carried out in advance of each installation. In case of doubt, calculations must be checked and approved by an expert (e.g.: structural engineer) before execution.

The building statics are not part of the calculation with SUNoptimo. The connection of the mounting system to the building (load-bearing capacity, roof cladding) must be assessed and checked by the installer, in cases of doubt with the help of external experts.

The technical regulations with the status used for the calculations in SUNoptimo are shown in the project report and must be checked by the executor to ensure that they are up to date. The installation instructions for TRIC mounting systems from Wagner must be observed, as well as the specifications of the module manufacturer and the relevant standards, guidelines and legal regulations.

Our General Terms and Conditions of Business apply to quotations, orders and any legal transactions arising from them in their current version. ( www.wagner-solar.com/agb)

13017

1480

1053

4

1

13028

Department	Tech. Reference

-	-

16143

Created by

Document type

-

Approved by

-

XXX

Title

Status

-

Project Number

1:311

2846

16008

25354

25441

3742

31027

5315

26772

5

2

3

751

986

MS-HMR-Kaplanova

###### Roof_1

Wa_DE_hmRtfwnq

Vers Created	Lang.	Page

##### R1  12/16/2024	DE	1/1

Tech. Reference

-

20  17

20  17

Department

-

20 20

20 20

2  20 19

2  20 19

4  19 19

4

4  19 19

3  20 20

3  20 20

2  20 21  20  21

2  20 21  20  21

21  20

21  20

21 11  20

21 11  20

11 11  20

5

11 11  20

11 20  1

11 20  1

21 21  4  21

21 21  4  21

Σ S87.47 kg Σ U150.26 kg

20	19

20	19

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S87.47 kg Σ U150.26 kg

6	21

6	21

Σ S100.22 kg Σ U150.26 kg

20	6

20	6

Σ S74.13 kg Σ U83.71 kg

Σ S74.13 kg Σ U83.71 kg

Σ S74.13 kg Σ U83.71 kg

Σ S100.22 kg Σ U150.26 kg

21	21

21	21

Σ S87.47 kg Σ U150.26 kg

20  15

Σ S69.72 kg Σ U83.71 kg

20 20  2

Σ S69.72 kg Σ U83.71 kg

20 20  11

11 11

Σ S69.72 kg Σ U83.71 kg

11

20 20

Σ S69.72 kg Σ U83.71 kg

1

21 21

Σ S87.47 kg Σ U150.26 kg

20  21

Σ S100.22 kg Σ U150.26 kg

21  21

21 11

Σ S74.13 kg Σ U83.71 kg

20

11 11

Σ S74.13 kg Σ U83.71 kg

20

11 11

Σ S74.13 kg Σ U83.71 kg

10

21 21

Σ S100.22 kg Σ U150.26 kg

21  21

20  15

20 20

2  20 20

11  11 11

11  20 20  1

21 21  20  21

21  21

21 11  20

11 11  20

11 11  10

21 21  21  21

20  17

20 20

2  20 19

4  19 19

3  20 20

2  20 21  20  21

21  18

21 20

2  20 21  5  21

21  21

21 21

21  21

20  17

20 20

2  20 19

4  19 19

3  20 20

2  20 21  20  21

21  18

21 20  2

20 21  5  21

21  21

21 21  21  21

Σ S87.47 kg

Σ S69.72 kg

Σ S69.72 kg

Σ S69.72 kg

Σ S69.72 kg

Σ S87.47 kg

Σ S136.55 kg

Σ S88.92 kg

Σ S136.55 kg

Σ S165.39 kg

Σ S165.39 kg

Σ U150.26 kg

20	19

20	19

Σ U83.71 kg

Σ U83.71 kg

1 Σ U83.71 kg

Σ U83.71 kg

Σ U150.26 kg

6	21

6	21

Σ U150.26 kg

14	14

14	14

2Σ U83.71 kg

Σ U150.26 kg

21

21

21

21

Σ U152.43 kg	Σ U152.43 kg

21	21 21	21

21	21 21	21

Σ S87.47 kg Σ U150.26 kg

20  15

20 20

Σ S69.72 kg Σ U83.71 kg

2

20 20

Σ S69.72 kg Σ U83.71 kg

11

11 11

Σ S69.72 kg Σ U83.71 kg

11

20 20

Σ S69.72 kg Σ U83.71 kg

1

21 21

Σ S87.47 kg Σ U150.26 kg

20  21

Σ S136.55 kg Σ U150.26 kg

21  21

21 11

Σ S88.92 kg Σ U83.71 kg

20

11 21

Σ S136.55 kg Σ U150.26 kg

20  21

Σ S165.39 kg Σ U152.43 kg

21  16

3

21 21

Σ S165.39 kg Σ U152.43 kg

21  21

20  15

20 20

2  20 20

11  11 11

11  20 20  1

21 21  20  21

21  21

21 11  20

11 21  20  21

21  16  21 21  21  21

Created by

Document type

-

Title

Approved by

-

1:311

Status

-

Project Number

Wa_DE_hmRtfwnq

Vers Created

R1  12/16/2024

MS-HMR-Kaplanova

Roof_1

Lang.	Page

DE

1/1

Total Uplift (U) 5023 kg Total Sliding (S) 4047 kg

Total Amount Stones 5094 (5,094 kg)

Tech. Reference

-

20  17

Department

-

20 20

2  20 19

4  19 19

3  20 20

2  20 21  20  21

21  20

21 11  20

11 11  20

11 20  1

21 21  4  21

20 50.4517kg/m² 20 20 33.252kg/m² 20 19 33.254kg/m² 19 19 33.253kg/m² 20 20 33.252kg/m² 20 21 49.9720kg/m² 21	21 49.7320kg/m² 21 11 33.2520kg/m² 11 11 33.2520kg/m² 11 20 33.251kg/m² 21 21 45.884kg/m²	21

| Σ U150.26 kg | Σ U83.71 kg |  |  | Σ U83.71 kg | Σ U150.26 kg | Σ U150.26 kg |
| --- | --- | --- | --- | --- | --- | --- |

Σ S87.47 kg

20 Area : 33	19

20 49.49 kg/m²	19

Σ S69.72 kg

Area : 34

33.25 kg/m²

Σ S69.72 kg Σ U83.71 kg

Area : 35

33.25 kg/m²

Σ S69.72 kg Σ U83.71 kg

4

Area : 36

33.25 kg/m²

Σ S69.72 kg

Area : 37

33.25 kg/m²

Σ S87.47 kg

6 Area : 38	21

6 49.97 kg/m²	21

Σ S100.22 kg

20 Area : 39	6

20 50.21 kg/m²	6

Σ S74.13 kg Σ U83.71 kg

Area : 40

33.25 kg/m²

Σ S74.13 kg Σ U83.71 kg

5

Area : 41

33.25 kg/m²

Σ S74.13 kg Σ U83.71 kg

Area : 42

33.25 kg/m²

Σ S100.22 kg Σ U150.26 kg

21

21

21

21

Area : 43

54.07 kg/m²

Σ S87.47 kg Σ U150.26 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S87.47 kg Σ U150.26 kg

Σ S100.22 kg Σ U150.26 kg

Σ S74.13 kg Σ U83.71 kg

Σ S74.13 kg Σ U83.71 kg

Σ S74.13 kg Σ U83.71 kg

Σ S100.22 kg Σ U150.26 kg

20 Are1a5: 22 20 20 Area2: 23 20 20 Are1a1: 24 11 11 Are1a1: 25 20 20 Area1: 26 21 21 Are2a0: 27 21	21 Are2a1: 28 21 11 Are2a0: 29 11 11 Are2a0: 30 11 11 Are1a0: 31 21 21 Are2a1: 32	21

20  15

20 20

2  20 20

11  11 11

11  20 20  1

21 21  20  21

21  21

21 11  20

11 11  20

11 11  10

21 21  21  21

20  17

20 20

2  20 19

4  19 19

3  20 20

2  20 21  20  21

21  18

21 20

2  20 21  5  21

21  21

21 21

21  21

20 50. 17kg/m² 20 20 33.252kg/

20 19 33.254kg/m² 19 19 33.253kg/m² 20 20 33.252kg/m² 20 21 49.9720kg/m²	21

21 49.2518kg/m² 21 20 33.252kg/m² 20 21 46.365kg/m²	21

21 54.072k1g/m² 21 21 54.072k1g/m²	21

1

|  | Σ S87.47 kg Σ U150.26 kg |  | Σ S69.72 kg Σ U83.71 kg | Σ S69.72 kg Σ U83.71 kg |
| --- | --- | --- | --- | --- |
| 20 | Area : 11 | 19 | Area : 12 | Area : 13 |
| 20 | 49.49 kg/m² | 19 | 33.25 kg/m² | 33.25 kg/m² |

Σ S69.72 kg

Σ S69.72 kg

Σ S87.47 kg

Σ S136.55 kg

Σ S88.92 kg

Σ S136.55 kg

Σ S165.39 kg

Σ S165.39 kg

Σ U83.71 kg

Area : 14

33.25 kg/m²

Σ U83.71 kg

Area : 15

33.25 kg/m²

Σ U150.26 kg

6 Area : 16	21

6 49.97 kg/m²	21

Σ U150.26 kg

14 Area : 17	14

14 50.7 kg/m²	14

Σ U83.71 kg

Area : 18

33.25 kg/m²

Σ U150.26 kg

21

21

Area : 19	21

53.59 kg/m²	21

Σ U152.43 kg	Σ U152.43 kg

21 Area : 20 21 21 Area : 21	21

21 51.66 kg/m² 21 21 54.07 kg/m²	21

2

3

Σ S87.47 kg Σ U150.26 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S69.72 kg Σ U83.71 kg

Σ S87.47 kg Σ U150.26 kg

Σ S136.55 kg Σ U150.26 kg

Σ S88.92 kg Σ U83.71 kg

Σ S136.55 kg Σ U150.26 kg

Σ S165.39 kg Σ U152.43 kg

Σ S165.39 kg Σ U152.43 kg

20 Ar1ea5: 0 20 20 Are2a : 1 20 20 Are1a1: 2 11 11 Are1a1: 3 20 20 Area1 : 4 21 21 Ar2ea0: 5	21

21 Are2a1: 6 21 11 Ar2ea0: 7 11 21 Ar2ea0: 8	21

21 Ar1ea6: 9 21 21 Are2a1: 10	21

20  15

20 20

2  20 20

11  11 11

11  20 20  1

21 21  20  21

21  21

21 11  20

11 21  20  21

21  16  21 21  21  21

Created by

XXX

Document type

-

Title

Approved by

-

1:311

Status

-

Project Number

Wa_DE_hmRtfwnq

Vers Created

R1  12/16/2024

MS-HMR-Kaplanova

Roof_1

Lang.	Page

DE

1/1

Total Uplift (U) 5023 kg Total Sliding (S) 4047 kg

Total Amount Stones 5094 (5,094 kg)

| 20 | 17 | 20 | 20 | 2 | 20 | 19 | 4 | 19 | 19 | 3 | 20 | 20 | 2 | 20 | 21 | 20 | 21 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 20 | 1750.45 kg/m² | 20 | 20 | 233.25 kg/m² | 20 | 19 | 433.25 kg/m² | 19 | 19 | 333.25 kg/m² | 20 | 20 | 233.25 kg/m² | 20 | 21 | 2409.97 kg/m² | 21 |

Tech. Reference

-

Σ S87.47 kg Σ U150.26 kg

20	Area : 11  19

20	49.49 kg/m²  19

Department

-

Σ S69.72 kg Σ U83.71 kg

Area : 12

33.25 kg/m²

Σ S69.72 kg Σ U83.71 kg

1

Area : 13

33.25 kg/m²

Σ S69.72 kg Σ U83.71 kg

Area : 14

33.25 kg/m²

Σ S69.72 kg Σ U83.71 kg

Area : 15

33.25 kg/m²

Σ S87.47 kg Σ U150.26 kg

6	Area : 16  21

6	49.97 kg/m²  21

Σ S87.47 kg Σ U150.26 kg

20	15Area : 0	20	20

Σ S69.72 kg Σ U83.71 kg

2Area : 1	20	20

Σ S69.72 kg Σ U83.71 kg

1A1rea : 2	11	11

Σ S69.72 kg Σ U83.71 kg

1A1rea : 3	20	20

Σ S69.72 kg Σ U83.71 kg

1Area : 4	21	21

Σ S87.47 kg Σ U150.26 kg

2A0rea : 5	21

Approved by

-

20	15

20	20

2	20	20

11	11	11

11	20

20	1

21	21	20	21

Created by

Document type

-

Title

-

Status

-

Project Number

Wa_DE_hmRtfwnq

Vers Created

R1  12/16/2024

Module area 1

Roof_1

Lang.	Page

DE

2/6

| 21 | 18 | 21 | 20 | 2 | 20 | 21 | 5 | 21 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 21 | 1849.25 kg/m² | 21 | 20 | 233.25 kg/m² | 20 | 21 | 546.36 kg/m² | 21 |

Department

-

Tech. Reference

-

Σ S136.55 kg Σ U150.26 kg

14	Area : 17	14

14	50.7 kg/m²	14

Σ S88.92 kg Σ U83.71 kg

2

Area : 18

33.25 kg/m²

Σ S136.55 kg Σ U150.26 kg

21	Area : 19	21

21	53.59 kg/m²	21

Σ S136.55 kg Σ U150.26 kg

21	2A1rea : 6	21	11

Approved by

-

21	21	21	11

Σ S88.92 kg Σ U83.71 kg

2A0rea : 7	11	21

20	11	21

Σ S136.55 kg Σ U150.26 kg

2A0rea : 8	21

20	21

Created by

Rusin

Document type

-

Title

-

Explicit

-

Project Number

Wa_DE_hmRtfwnq

Vers Created

R1  12/16/2024

Module area 2

Roof_1

Lang.	Page

DE

3/6

21

21

21

21

21

21

Σ S165.39 kg

21

21

514.

2

21

Department

-

07 kg/m²

Tech. Reference

-

3

Σ U152.43 kg

21

21

21

Area : 20

21

21

21

51.66 kg/m²

07 kg/m²

Σ S165.39 kg Σ U152.43 kg

21

21

514.

2

Area : 21

21

54.07 kg/m²

Created by

Rusin

Document type

-

Title

-

Explicit

-

Project Number

Wa_DE_hmRtfwnq

Vers Created

R1  12/16/2024

Module area 3

Roof_1

Lang.	Page

DE

4/6

Σ S165.39 kg Σ U152.43 kg

Σ S165.39 kg Σ U152.43 kg

21

2

21

21

1

21

Approved by

-

6Area : 9	A1rea : 10

21

16

21

21

21

21

| 20 | 17 | 20 | 20 | 2 | 20 | 19 | 4 | 19 | 19 | 3 | 20 | 20 | 2 | 20 | 21 | 20 | 21 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 20 | 1750.45 kg/m² | 20 | 20 | 233.25 kg/m² | 20 | 19 | 433.25 kg/m² | 19 | 19 | 333.25 kg/m² | 20 | 20 | 233.25 kg/m² | 20 | 21 | 2409.97 kg/m² | 21 |

Tech. Reference

-

Σ S87.47 kg Σ U150.26 kg

20	Area : 33  19

20	49.49 kg/m²  19

Department

-

Σ S69.72 kg Σ U83.71 kg

Area : 34

33.25 kg/m²

Σ S69.72 kg Σ U83.71 kg

4

Area : 35

33.25 kg/m²

Σ S69.72 kg Σ U83.71 kg

Area : 36

33.25 kg/m²

Σ S69.72 kg Σ U83.71 kg

Area : 37

33.25 kg/m²

Σ S87.47 kg Σ U150.26 kg

6	Area : 38  21

6	49.97 kg/m²  21

Σ S87.47 kg Σ U150.26 kg

20	15Area : 22 20	20

Σ S69.72 kg Σ U83.71 kg

2Area : 23  20	20

Σ S69.72 kg Σ U83.71 kg

1A1rea : 24  11	11

Σ S69.72 kg Σ U83.71 kg

1A1rea : 25 20	20

Σ S69.72 kg Σ U83.71 kg

1Area : 26  21	21

Σ S87.47 kg Σ U150.26 kg

2A0rea : 27  21

Approved by

-

20	15

20	20

2	20	20

11	11	11

11	20

20	1

21	21	20	21

Created by

Rusin

Document type

-

Title

-

Explicit

-

Project Number

Wa_DE_hmRtfwnq

Vers Created

R1  12/16/2024

Module area 4

Roof_1

Lang.	Page

DE

5/6

| 21 | 20 | 21 | 11 | 20 | 11 | 11 | 20 | 11 | 20 | 1 | 21 | 21 | 4 | 21 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 21 | 2409.73 kg/m² | 21 | 11 | 2303.25 kg/m² | 11 | 11 | 2303.25 kg/m² | 11 | 20 | 133.25 kg/m² | 21 | 21 | 445.88 kg/m² | 21 |

Department

-

Tech. Reference

-

Σ S100.22 kg Σ U150.26 kg

20	Area : 39	6

Σ S74.13 kg Σ U83.71 kg

Area : 40

Σ S74.13 kg Σ U83.71 kg

5

Area : 41

Σ S74.13 kg Σ U83.71 kg

Area : 42

Σ S100.22 kg Σ U150.26 kg

21	Area : 43	21

20	50.21 kg/m²	6

33.25 kg/m²

33.25 kg/m²

33.25 kg/m²

21	54.07 kg/m²	21

Σ S100.22 kg Σ U150.26 kg

21	2A1rea : 28	21	11

Approved by

-

21	21	21	11

Σ S74.13 kg Σ U83.71 kg

2A0rea : 29	11	11

#### 20	11	11

Σ S74.13 kg Σ U83.71 kg

2A0rea : 30	11	11

#### 20	11	11

Σ S74.13 kg Σ U83.71 kg

10Area : 31	21	21

#### 10	21	21

Σ S100.22 kg Σ U150.26 kg

2A1rea : 32	21

21	21

Created by

Rusin

Document type

-

Title

-

Explicit

-

Project Number

Wa_DE_hmRtfwnq

Vers Created

R1  12/16/2024

Module area 5

Roof_1

Lang.	Page

DE

6/6